국문제목

<10 포인트, 태그래픽>

지철근*, 오기봉** <국문성명, 8 포인트, 신그래픽, 발표자에 밑줄>

서울대*, 서울과학기술대** <국문소속 ,8 포인트, 신그래픽>

영문제목

<8 포인트, 신그래픽>

Chol-Kon Chee*, Kie-Bong Oh** <영문성명, 8 포인트, 신그래픽>

Seoul University*, Seoul National University** <영문소속,  8 포인트, 신그래픽>

Abstract - This paper gives a basic data of fluorescent lamp equipments for calculating of receiving capacity. The fluorescent lamp equipment has non-linear characteristics of the active and the reactive power variation. Therefore we need real measurements. We tested and measured active and reactive power of fluorescent lamp equipments which use 40[W] lamps and various ballasts. The potential variation range is A.C. 200～240[V].

2018년도 조명·전기설비학회 추계학술대회 논문집 2018. 11. 9.

<작성방법 : 요약은 반드시 영문으로 작성, 8 포인트, 신명조.>

1. 서    론

건축물이 점차 대형화하여 감에 따라 건축물에서 사용하는 전기용량도 증가하고 있으며, 생산성을 고려한 조명환경의 개선에따른 조명용 전력이 크게 증가하는 추세에 있다. 특히 업무용 빌딩의 경우는 조명용 전력의 비중이 대단히 높게 나타나고 있으며, 형광등이 대부분 사용되고 있다[1].

‥‥‥‥‥‥‥‥‥‥‥‥(중략)‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥

<작성방법 :  본문내용 8 포인트 , 신명조>

2. 본    론

2.1. 측정대상

T10/40[W] 형광램프를 사용하는 글로    ‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥(중략)‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥

2.2. 측정방법

등기구의 입력단에 전압, 전류, 역률, 유효전력 및 무효전력을 동시에 측정할 수 있는 디지털 계측기를 부착하고, 슬라이닥스를 사용하여 전원전압을 200부터 240[V]까지 10[V] 단위로 증가시키며 측정하였다.

측정램프는 표준램프에 근사한 1개를 선택하여 계속 사용하였으며, ‥‥‥‥‥‥‥‥‥‥‥‥(중략)‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥.

2.3. 측정결과

그림 1. 실험계의 개략도

Fig. 1. Schematic diagram of the experimental set-up

측정한 결과를 분석하여 보면 유효전력의 경우 정격전압 220[V]를 기준으로 하면 변동폭이 가장 큰 것은 글로 스타터식 안정기로 80～118[%]의 범위에서 변동하였으며, 그 다음은 래피드 스타트식 안정기로 87～117[%]의 범위에서 변화하였으며, ‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥(중략)‥‥‥‥‥‥‥‥‥‥‥‥‥

표 1에 안정기의 종류에 따른 조도 측정결과의 평균치를, 표 2에 안정기의 종류에 따른 상대 광효율 측정치의 평균치를 나타내었다.

표  1. 전원전압 변동에 따른 안정기의 [lx/W] 변화

Table 1. Variation of [lx/W] of various ballast type

전압[V]	글로 스타터식 [lx/W]	래피드 스타트식 [lx/W]	절전형 자기식 [lx/W]	전자식 [lx/W]
200	6.09	5.77	6.36	6.82
210	5.84	5.67	6.37	6.83
220	5.75	5.58	6.31	6.82

3. 결    론

전자식 안정기를 사용하는 것이 바람직한 것으로 조사되었다.    형광램프를 대규모로 사용하는 장소의 경우 수전용량 산정시 전원전압변동에 따른 등기구의 유효, 무효전력 변화를 고려하는 것이 바람직한 것으로 사료된다.

감사의 글

‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥

‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥‥

참 고 문 헌

[1] Bok-Hee Lee and Seung-Chil Lee, The Major Foundational Technics for Grounding Systems, Uije Publication Ltd., pp. 37-51, 1999.

[2] A. Phillips, Guide for Transmission Line Grounding: A Roadmap for Design, Testing, and Remediation: Part .

<작성순서 : 저자명, 논문제목, 논문지명, 권호, 페이지, 출판년도>

<작성방법 : 참고문헌은 가능한 영문으로 작성, 8 포인트, 신명조>